## Slide 1
Design and Eco-techno-economic Analyses of SOFC/Gas Turbine Hybrid Systems Accounting for Long-Term Degradation
ESCAPE 30
September, 2020
Haoxiang (Hundey) Lai a
Nor Farida Harun b
David Tucker b
Thomas A. Adams II a*
a McMaster University, Department of Chemical Engineering, Hamilton, ON, Canada
b US Department of Energy, National Energy Technology Laboratory, Morgantown, WV, USA
* Corresponding Author. tadams@mcmaster.ca

## Slide 2
SOFC Overview
High electrical efficiency ~60% (cell level)
Lower greenhouse gas emission than conventional power plant (coal/natural gas power plant)
Sources: U.S. DOE, Also: Materials System Research, Inc.
Adams, Nease, Tucker, & Barton. I&EC Research (2013)

## Slide 3
Research Motivation
Challenge: SOFC degrades over time
Operating Mode | Constant Power Mode | Constant Voltage Mode
SOFC Degradation | Fast (and increasing) | Slow
Lifetime | Up to ~1.5 years | 13 – 14 years
Power output | Constant (baseload power) | Decreasing, not useful for baseload
Fuel | Increasing fuel flow | Increasing unspent fuel flow
New!
    For baseload power production, one solution is to be coupled with gas turbine (GT) in a SOFC/GT hybrid system* Key discovery
Source: Tucker Sepulveda, and Harun, Journal of Fuel Cell Science and Technology (2014)

## Slide 4
SOFC/GT Hybrid System
Operated in constant voltage mode
Power decreases as SOFC degrades
Over-size turbine (sized at the end of lifetime of SOFC)
Power increases to almost make up for the SOFC power losses

## Slide 5
Research Goal
We would like to answer whether it is better to have
An SOFC standalone plant (Case i)
SOFC constant power mode, replace SOFC more frequently (short lifetime)
2. An SOFC/GT hybrid plant (more expensive) (Case ii)
SOFC constant voltage mode, replace SOFC less frequently (much longer lifetime)
Plant scale: 550 MW Plant lifetime: 30 years
The first system-level eco-techno-economic analysis of SOFC/GT hybrid plant accounting for long-term degradation
Contribution to the early large-scale adoption of SOFC from a system-level perspective

## Slide 6
SOFC Standalone Plant (Case i)

## Slide 7
SOFC/GT Hybrid Plant (Case ii)
Aspen Plus steady-state model
Dynamic model*, pause in each time step (weekly)
Integrate models by using interfaces:
Aspen Excel Workbook & VBA
Matlab
Pseudo steady-state approach
Source: Zaccaria, Tucker, and Traverso, Journal of Power Sources (2016)

## Slide 8
Results
SOFC Standalone Plant (Case i)
SOFC lifetime: ~ 3132 hours = ~ 19 weeks
Constant power and fuel utilization

## Slide 9
Results
SOFC/GT Hybrid Plant (Case ii)
SOFC lifetime: ~ 351 weeks = ~ 6.7 years
Constant power and fuel utilization

## Slide 10
Results
 | SOFC Standalone Plant | SOFC/GT Hybrid Plant
SOFC Stack Efficiency (LHV) | 57.9 % | 66.2 %
Overall Plant Efficiency (LHV) | 30.7 % | 41.8 %
First year Capital Cost ($ Million) | $7,216 | $4,129
Average Annual SOFC Replacement Cost ($ Million) | $3,048 | $109
Annual Material, Operating and Maintenance Cost ($ Million) | $421 | $398
LCOE ($/MWh) | $426 | $85
CO2 Emission (kg/MWh) | 673 | 493
For plant lifetime of 30 years

## Slide 11
Conclusion
Proposed and designed SOFC Standalone plant (Case i) and SOFC/GT Hybrid plant (Case ii)
Model simulations with a pseudo steady-state approach
The result of eco-techno-economic analysis shows that SOFC/GT Hybrid plant has higher efficiency, lower costs, and lower greenhouse gas emission.
SOFC/GT Hybrid can be a promising near-term approach for baseload power production
Future Work
Design and investigate cases with steam bottoming cycle
Optimize the replacement time of SOFC stack (SOFC lifetime) in the hybrid case
Sensitivity analysis

## Slide 12
Thank you
Acknowledgements